## Slide 1
Duct Design Manual Calculation
(Air Distribution System)
Engr. NICK JOHNSONN FERNANDEZ
Technical Committee Member, PSIM Makati
Partner Consultant, RBSanchez PME Consultants and Associates, Inc.
Technical Design & Operations Consultant, Metallurgical and Mining
Technical Seminar Partners:
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa
Follow me on LinkedIn
Scan the code using
LinkedIn Mobile

## Slide 2
About the Speaker
    Worked as a freelance mechanical designer, modeler, and researcher for a variety of local and international companies since 2013.
    Graduated with a BS in Mechanical Engineering from President Ramon Magsaysay State University in 2018.
    Started my professional career in 2018 at RBSanchez PME Consultants and Associates, Inc.
    Currently, Independent Design and Operations Consultant for Various Industrial and Mining Companies
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa

## Slide 3
About the Speaker
    Currently, Partner Consultant and the former Director of Engineering & Numerical Simulations — Onshore and Offshore at RBSanchez PME Consultants
    Handled and led various multi-discipline (i.e., MEP, civil, geological, mining and metallurgical) critical projects for RBSanchez PME.
    Member, ASHRAE
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa

## Slide 4
About the Speaker
    Team Member – Applications Engineer at Digital Creatives Worldwide since 2022
    Autodesk Certified Instructor (ACI)
    Autodesk Certified User: AutoCAD and Autodesk Inventor
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa

## Slide 5
About the Speaker
    Distant Learning Specializations
    MicroMasters Course in Optimization Principles and Algorithms, Swiss Federal Institute of Technology
    Professional Degree Course in Data Science and Analytics PH125.x, HarvardX
    Data Science and Analytics Specialization, John Hopkins University
    Sustainable Building Design MIT4.464x, MITx
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa

## Slide 6
Learning Objectives:
    To learn the theories and principle of duct design
    To learn the basics of duct design, computation of external static pressure (ESP), pressure losses.
    To learn how to use friction charts for friction loss determination
    To learn how to use various software to determine friction loss such as spreadsheets, duct sizers, and ASHRAE databases.
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa

## Slide 7
Introduction to Duct Design
    Ducts in air distribution systems are designed to transport volume of air as efficiently and quietly as possible to minimize energy consumption and excessive noise.
    Duct designs are also intricate in the sense where proper layout of the system and terminals are important to deliver the air minimizing the air stagnation (“age of air”) over the space.
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa

## Slide 8
Important Aspects of Duct System Design
    Duct Layout
    Fittings
    Leakage
    Acoustics
    Equipment Selection
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa

## Slide 9
Main Goals of Duct Design
    To design energy-efficient HVAC system while minimizing the capital (first) cost and operational expenses.
    To provide comprehensive design and a high-quality project with minimum construction cost.
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa

## Slide 10
Pressure Loss
    The basis of duct design is the identification and summation of pressure loss in each sections of the duct. The pressure loss can be determined using the Darcy-Weisbach equation which states that:
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa

## Slide 11
Pressure Loss
    Or can be written as;
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa
    Resistance to air flow due to friction
    Dynamic losses due to velocity

## Slide 12
Pressure Loss
    Or can be written as;
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa
    Darcy
    Weisbach
    It can be calculated by hand
    Friction chart
    Duct fitting database
    It can be calculated by hand

## Slide 13
Conservation of Mass
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa
Conservation of Energy

## Slide 14
Conservation of Mass
    To establish the flowrate within ducts, conservation of mass shall be used. This law of conservation of mass considers that the mass flow rate into the duct must be equal to that mass flow rate going out the section, considering (no mass is added or lost – in other words “leakage”).
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa

## Slide 15
Conservation of Mass:
    Continuity Equation
    Considering that the air density is constant in a duct system, the volumetric flow rate at any duct section is
    Where;
    duct area
    fluid velocity
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa

## Slide 16
Conservation of Mass:
    Diverging Flow
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa
    Converging Flow

## Slide 17
Conservation of Energy
    Pressure losses in a duct system due to friction and other dynamic effects must be compensated by energy added to the flow by means of a fan.
    So, in HVAC system, the total energy per air volume is:
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa

## Slide 18
Conservation of Energy
    And this equation can be converted to pressure terms, as
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa
METRIC
U.S.

## Slide 19
Conservation of Energy
    For air to move, a pressure differential must exist.
    Air moves from high to low pressure area. For example, a fan inlet is a negative pressure area, and the fan outlet is a positive pressure area.
    Positive pressure flows are also called “supply air”;
    Negative pressure flows are also called “exhaust” or “return air”.
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa

## Slide 20
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa
Pressure Changes

## Slide 21
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa
Different Methods in Duct Design
    Equal friction method
    - Calculates each section’s duct diameter from friction chart or databases.
    2. Static Regain method
    - calculates the duct diameter for each section with each
    3. Constant Velocity method

## Slide 22
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa
Solving the Darcy Equation
    To calculate the resistance of straight duct, including the friction factor “f”, the equations are as follows;
    Hydraulic Diameter
    Reynold’s Number

## Slide 23
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa
Solving the Darcy Equation
    Determine the friction loss of 20’ of Ø22” spiral round duct at an airflow rate of 5000 cfm with an elevation of 5400 ft above sea level.
    Use:
    0.061 lbm per ft3
    0.000734 lbm per ft-min
    0.0003 ft

## Slide 24
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa
Solving the Darcy Equation
    Determine the friction loss of 20’ of Ø22” spiral round duct at an airflow rate of 5000 cfm with an elevation of 5400 ft above sea level.
    Solution:

## Slide 25
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa
Solving the Darcy Equation
    Determine the friction loss of 20’ of Ø22” spiral round duct at an airflow rate of 5000 cfm with an elevation of 5400 ft above sea level.
    f = 0.0160

## Slide 26
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa
Solving the Darcy Equation
    Determine the friction loss of 20’ of Ø22” spiral round duct at an airflow rate of 5000 cfm at sea level pressure.
    (70F / 0%RH or 68F / 50% RH)
    Use:
    0.075 lbm per ft3
    0.000734 lbm per ft-min
    0.0003 ft

## Slide 27
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa

## Slide 28
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa
Actual Calculation of ESP

## Slide 29
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa
Using the Manual Calculation/Spreadsheet
    If the density is within the standard sea level pressure, determination of friction loss by hand:
    where:
    in cfm
    in inches
    in ft
    in inches Wg

## Slide 30
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa
External Static Pressure (ESP)
Ventilation Calculation
5 CFM per person
10 pax per 1000 ft2
Q = 5 x (10 / 1000) x 344.48
Q = 17.22 cfm
0.06 cfm per ft2
Q = 0.06 x 344.48
Q = 20.67

## Slide 31
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa
External Static Pressure (ESP)
Ventilation Calculation
Qt = 17.22 + 20.67 =
= 37.89 (1.30)
= 49.26 cfm say 50 cfm
Use friction chart.
Use database.
Use spreadsheet.

## Slide 32
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa
External Static Pressure (ESP)
Flow Rate | Velocity | Equivalent Diameter | Duct Size (Width) | Duct Size (Height) | Aspect Ratio | Head Loss
CFM | FPM | in (mm) | in (mm) | in (mm) | - | in. Wg / 100 ft
50 | 1000 | 3 (75) | 4 (100) | 2 (50) | 2:1 | 0.720
50 | 1000 | 3 (75) | 3 (75) | 3 (75) | 1:1 | 0.496
50 | 573 | 4 (100) | 5 (125) | 3 (75) | 5:3 | 0.145
50 | 573 | 4 (100) | 4 (100) | 3 (75) | 4:3 | 0.245
50 | 573 | 4 (100) | 7 (175) | 2 (50) | 7:2 | 0.207
50 | 573 | 4 (100) | 6 (150) | 2 (50) | 3:1 | 0.289
50 | 367 | 5 (125) | 5 (125) | 4 (100) | 5:4 | 0.069
50 | 367 | 5 (125) | 7 (175) | 3 (75) | 7:3 | 0.068

## Slide 33
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa
Consideration of Surface Area
Equivalent Diameter | Duct Size (Width) | Duct Size (Height) | Aspect Ratio | Head Loss | Surface Area
in (mm) | in (mm) | in (mm) | - | in. Wg / 100 ft | in2 (mm2)
3 (75) | 4 (100) | 2 (50) | 2:1 | 0.720 | 12 (300)
3 (75) | 3 (75) | 3 (75) | 1:1 | 0.496 | 12 (300)
4 (100) | 5 (125) | 3 (75) | 5:3 | 0.145 | 16 (400)
4 (100) | 4 (100) | 3 (75) | 4:3 | 0.245 | 14 (350)
4 (100) | 7 (175) | 2 (50) | 7:2 | 0.207 | 18 (450)
4 (100) | 6 (150) | 2 (50) | 3:1 | 0.289 | 16 (400)
5 (125) | 5 (125) | 4 (100) | 5:4 | 0.069 | 18 (450)
5 (125) | 7 (175) | 3 (75) | 7:3 | 0.068 | 20 (500)

## Slide 34
Selection of Duct Size
    Check the lowest friction or pressure drop in the table of duct sizes.
    Consider the material used in each duct sizes (this includes weight of the material for hangar supports).
    Select the balance of friction drop and material used.
    Note that, pressure drop relates to the equipment size (i.e., motor, case size, etc.) and cost.
    Note that, material used relates to the duct weight, installation, and material cost.
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa

## Slide 35
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa
Presentation of ASHRAE Database
Presentation of Duct Fittings
Presentation of Various Duct Fitting Drawing

## Slide 36
Simulations-Based Design for Duct Design and Terminal Location
Engr. NICK JOHNSONN FERNANDEZ
Technical Committee Member, PSIM Makati
Partner Consultant, RBSanchez PME Consultants and Associates, Inc.
Technical Design & Operations Consultant, Metallurgical and Mining
Technical Seminar Partners:
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa
Follow me on LinkedIn
Scan the code using
LinkedIn Mobile

## Slide 37
Learning Objectives:
    To apply and size duct works using software such as advanced spreadsheets, ASHRAE database.
    To learn how to use LISP in ductwork drafting.
    To utilize dwg drawings to increase productivity on duct sizing and ESP determination.
    To understand the proper duct design related to terminal selection and location.
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa

## Slide 38
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa
Actual Simulation, Drafting Techniques and Presentation

## Slide 39
Simulations-Based Design for Pipe Design
Engr. NICK JOHNSONN FERNANDEZ
Technical Committee Member, PSIM Makati
Partner Consultant, RBSanchez PME Consultants and Associates, Inc.
Technical Design & Operations Consultant, Metallurgical and Mining
Technical Seminar Partners:
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa
Follow me on LinkedIn
Scan the code using
LinkedIn Mobile

## Slide 40
Learning Objectives:
    To apply and size pipe works using basic numerical simulation and other pipe design software such as Fluid Flow.
    To learn how to utilize the software to size up pipes with selected pumps or indicated initial flow requirement
    To improve the pipe layout drafting to augment the manual design pipe size calculations.
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa

## Slide 41
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa
Actual Simulation, Drafting Techniques and Presentation

## Slide 42
Technical Seminar Partners:
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa
Question and Answer?

## Slide 43
Technical Seminar Partners:
PSIM Makati HVAC Series | TECHNICAL SEMINAR
March 9,16,23 and April 13
PHILIPPINE TRADE TRAINING CENTER, PASAY CITY
Education/Study Tour Venue:
Vista Mall Sta Rosa
Thank You!
Follow me on LinkedIn
Scan the code using
LinkedIn Mobile